Building Maintenance Checklist

InspectionReport.app — Comprehensive Facility Inspection

Building / Facility: _______________

Inspector: _______________

Date: _______________

Weather Conditions: _______________

HVAC System

| Inspection Item | Frequency | Inspection Criteria / Method | Pass / Fail | Notes |
| --- | --- | --- | --- | --- |
| Inspect air handling units (AHU) | Monthly | Check filters, belts, motors for wear; listen for unusual noise |  |  |
| Replace HVAC air filters | Monthly | Replace disposable filters; clean permanent filters |  |  |
| Check thermostat calibration | Quarterly | Compare setpoint vs actual temp; differential ±1°C |  |  |
| Inspect condenser coils | Quarterly | Clean debris from coils; check refrigerant pressure |  |  |
| Test emergency shut-off | Annually | Verify HVAC emergency stop functions correctly |  |  |
| Lubricate fan bearings | Quarterly | Apply grease per manufacturer spec; check for play |  |  |
| Inspect ductwork for leaks | Annually | Visual check for gaps, tears, or disconnected sections |  |  |

Electrical System

| Inspection Item | Frequency | Inspection Criteria / Method | Pass / Fail | Notes |
| --- | --- | --- | --- | --- |
| Test RCD/GFCI protection devices | Monthly | Press test button; verify tripping within spec (<40ms) |  |  |
| Inspect distribution board | Quarterly | Check for overheating, corrosion, loose connections |  |  |
| Verify emergency lighting | Monthly | Full 30-sec functional test per BS 5266 (see separate checklist) |  |  |
| Inspect cable trays & conduits | Annually | Check for physical damage, corrosion, or overloaded trays |  |  |
| Test generator / UPS | Monthly | Run for 30 min under load; check fuel level and battery |  |  |
| Thermal imaging of switchgear | Annually | Scan for hot spots; investigate any ΔT >10°C |  |  |
| Inspect external lighting | Quarterly | Check photocell operation; replace failed lamps |  |  |

Plumbing System

| Inspection Item | Frequency | Inspection Criteria / Method | Pass / Fail | Notes |
| --- | --- | --- | --- | --- |
| Inspect visible pipes for leaks | Monthly | Check joints, valves, and fixtures for drips or corrosion |  |  |
| Test water pressure | Quarterly | Verify 3-5 bar; check pressure reducing valve operation |  |  |
| Inspect toilet cisterns & flush valves | Quarterly | Check for running water, flush volume, and seals |  |  |
| Clean drain traps & floor gullies | Monthly | Remove debris; pour water to maintain trap seal |  |  |
| Test emergency shut-off valves | Annually | Verify each valve closes fully and re-opens |  |  |
| Inspect water heater / boiler | Annually | Check T&P relief valve, anode rod, sediment drain |  |  |
| Test sump pump operation | Quarterly | Pour water into pit; verify auto-start and discharge |  |  |

Fire Safety Systems

| Inspection Item | Frequency | Inspection Criteria / Method | Pass / Fail | Notes |
| --- | --- | --- | --- | --- |
| Inspect fire extinguishers | Monthly | Check pressure gauge in green zone; no visible damage; pin intact |  |  |
| Test smoke / heat detectors | Monthly | Press test button; verify alarm panel signals |  |  |
| Inspect emergency exit signs | Monthly | Check illumination; verify correct directional arrows |  |  |
| Test fire alarm panel | Weekly | Check panel for fault/disable LEDs; silence any alarms |  |  |
| Inspect sprinkler heads | Quarterly | Check for obstructions, paint overspray, mechanical damage |  |  |
| Test fire doors & closers | Quarterly | Door closes fully from ½ open; latch engages; no wedges |  |  |
| Conduct fire drill | Annually | Full evacuation drill; record assembly time |  |  |

Structural Systems

| Inspection Item | Frequency | Inspection Criteria / Method | Pass / Fail | Notes |
| --- | --- | --- | --- | --- |
| Inspect walls for cracks | Quarterly | Note any new or widening cracks >2mm; monitor existing |  |  |
| Check ceiling for water stains | Monthly | Investigate any new staining for roof/pipe leaks |  |  |
| Inspect floor surfaces | Quarterly | Check for trip hazards, loose tiles, damaged covering |  |  |
| Check stair treads & handrails | Monthly | Verify secure fixings; check handrail height (900-1000mm) |  |  |
| Inspect roof for damage | Quarterly | Check for missing tiles, ponding water, membrane damage |  |  |

Exterior & Grounds

| Inspection Item | Frequency | Inspection Criteria / Method | Pass / Fail | Notes |
| --- | --- | --- | --- | --- |
| Inspect perimeter fencing / gates | Monthly | Check gates operate; no security breaches or damage |  |  |
| Check parking lot lighting | Monthly | Replace failed lamps; check timer/photocell |  |  |
| Inspect gutters & downpipes | Quarterly | Clear debris; check for blockages and secure fixings |  |  |
| Check exterior signage | Quarterly | Verify legibility; repair any damage or fading |  |  |
| Inspect paving & walkways | Quarterly | Repair trip hazards; fill cracks; check drainage |  |  |
| Test security cameras / CCTV | Monthly | Check image quality; verify recording; clean lenses |  |  |

Sign-Off & Certification

| Inspector Name: |  | Date: |  |
| --- | --- | --- | --- |
| Signature: |  | Reviewed By: |  |
| Next Inspection Due: |  | Review Date: |  |