InspectionReport

Ammonia Refrigeration PSM Compliance Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

Refrigeration Engine Room - General Condition

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Are all engine room access points clearly marked with 'Anhydrous Ammonia - Authorized Personnel Only' signage? | ☐ | ☐ | ☐ | ____________________ |
| Verify the engine room ventilation system is operational and providing adequate air changes per hour (min. 6 ACH). Check airflow with an anemometer. | ☐ | ☐ | ☐ | ____________________ |
| Confirm the emergency shutdown (ESD) switch is easily accessible, clearly labeled, and functional. Test the ESD monthly and record results. | ☐ | ☐ | ☐ | ____________________ |
| Check that ammonia sensors are properly calibrated (within the last 6 months) and positioned at appropriate locations (e.g., near potential leak sources, low points). | ☐ | ☐ | ☐ | ____________________ |
| Inspect for any signs of ammonia leaks (odor, white vapor, oil spots) around flanges, valves, and equipment. Use an ammonia leak detector to verify. | ☐ | ☐ | ☐ | ____________________ |
| Ensure adequate lighting (minimum 50 foot-candles) is provided throughout the engine room for safe operation and maintenance. | ☐ | ☐ | ☐ | ____________________ |
| Verify the engine room is free of obstructions, debris, and combustible materials. Maintain clear walkways and access to equipment. | ☐ | ☐ | ☐ | ____________________ |
| Confirm that appropriate warning signs (e.g., 'Danger - Anhydrous Ammonia', 'PPE Required') are prominently displayed. | ☐ | ☐ | ☐ | ____________________ |
| Inspect the emergency eyewash station and safety shower for proper function (minimum 15 minutes of continuous flow). Ensure the water is tepid (60-100°F). | ☐ | ☐ | ☐ | ____________________ |
| Verify the wind sock is in good condition and clearly visible to indicate wind direction in case of a release. | ☐ | ☐ | ☐ | ____________________ |

Piping and Vessels

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Visually inspect all ammonia piping for signs of corrosion, pitting, or thinning. Pay close attention to areas near welds and supports. | ☐ | ☐ | ☐ | ____________________ |
| Verify that pipe supports are properly installed and maintained to prevent excessive stress on piping. | ☐ | ☐ | ☐ | ____________________ |
| Inspect insulation on cold piping for damage or deterioration. Damaged insulation can lead to ice formation and corrosion under insulation (CUI). | ☐ | ☐ | ☐ | ____________________ |
| Confirm that pressure relief valves (PRVs) are properly sized, installed, and have current certification tags. Verify discharge piping is directed to a safe location. | ☐ | ☐ | ☐ | ____________________ |
| Inspect ammonia vessels (e.g., receivers, accumulators) for signs of bulging, dents, or other damage. Review vessel inspection records for compliance. | ☐ | ☐ | ☐ | ____________________ |
| Operate critical valves (e.g., isolation valves, control valves) to ensure they function smoothly and do not leak. Lubricate valve stems as needed. | ☐ | ☐ | ☐ | ____________________ |
| Check all flanged connections for leaks using an ammonia leak detector. Tighten bolts as necessary, following proper torque specifications. | ☐ | ☐ | ☐ | ____________________ |
| Ensure that all equipment nameplates are legible and contain accurate information (e.g., pressure rating, serial number). | ☐ | ☐ | ☐ | ____________________ |
| Verify oil pots on compressors are at the correct level and the oil is clean. Document oil changes. | ☐ | ☐ | ☐ | ____________________ |
| Confirm the non-condensable gas purge system is functional and properly removing air from the system. | ☐ | ☐ | ☐ | ____________________ |

Personal Protective Equipment (PPE) and Emergency Response

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify that appropriate PPE (e.g., ammonia-rated respirators, gloves, eye protection, chemical suits) is readily available and in good condition. | ☐ | ☐ | ☐ | ____________________ |
| Confirm that all personnel who may need to use respirators have been properly fit-tested within the last year. | ☐ | ☐ | ☐ | ____________________ |
| Review the emergency response plan for ammonia releases. Ensure it is up-to-date and readily accessible. | ☐ | ☐ | ☐ | ____________________ |
| Verify that first aid supplies specific to ammonia exposure (e.g., sterile saline solution for eye irrigation) are available. | ☐ | ☐ | ☐ | ____________________ |
| Check that the communication system (e.g., radios, alarms) is functional and can be used to alert personnel in case of an emergency. | ☐ | ☐ | ☐ | ____________________ |
| Ensure that evacuation routes are clearly marked and unobstructed. | ☐ | ☐ | ☐ | ____________________ |
| Inspect fire extinguishers for proper charge and current inspection tags. Ensure personnel are trained in their use. | ☐ | ☐ | ☐ | ____________________ |
| Verify that spill control materials (e.g., absorbent pads, neutralizing agents) are readily available in case of an ammonia release. | ☐ | ☐ | ☐ | ____________________ |
| Confirm that emergency drills are conducted regularly (at least annually) to practice the emergency response plan. | ☐ | ☐ | ☐ | ____________________ |
| Verify that contact information for the local HAZMAT team is readily available. | ☐ | ☐ | ☐ | ____________________ |

Documentation and Training

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify that the PSM program is up-to-date and includes all required elements (e.g., process safety information, hazard analysis, operating procedures). | ☐ | ☐ | ☐ | ____________________ |
| Review operating procedures for all phases of operation (startup, shutdown, normal operation, emergency operation). Ensure procedures are readily available to operators. | ☐ | ☐ | ☐ | ____________________ |
| Inspect maintenance records for all critical equipment (e.g., compressors, pumps, valves). Verify that maintenance is performed according to schedule. | ☐ | ☐ | ☐ | ____________________ |
| Verify that all personnel involved in the operation and maintenance of the ammonia refrigeration system have received adequate training. Review training records. | ☐ | ☐ | ☐ | ____________________ |
| Review the most recent Process Hazard Analysis (PHA) for the ammonia refrigeration system. Ensure that recommendations from the PHA have been implemented. | ☐ | ☐ | ☐ | ____________________ |
| Verify that a Management of Change (MOC) process is in place and followed for any changes to the ammonia refrigeration system. | ☐ | ☐ | ☐ | ____________________ |
| Review the mechanical integrity program for the ammonia refrigeration system. Ensure that inspections and tests are performed according to schedule. | ☐ | ☐ | ☐ | ____________________ |
| Verify that contractors working on the ammonia refrigeration system are aware of the hazards and have received appropriate training. | ☐ | ☐ | ☐ | ____________________ |
| Confirm that a Pre-Startup Safety Review (PSSR) is conducted after any significant modifications to the ammonia refrigeration system. | ☐ | ☐ | ☐ | ____________________ |
| Review incident investigation reports for any incidents involving the ammonia refrigeration system. Ensure that corrective actions have been implemented. | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________