InspectionReport

Emergency Light Inspection Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

Jurisdiction: US. NFPA 101 and OSHA 29 CFR 1910.37 are US standards. The checklist is US-focused but the testing principles are broadly applicable.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

Inspection header

| Field | Entry |
| --- | --- |
| Facility name and address | ________________________________________________ |
| Inspector name and date | ________________________________________________ |
| Inspection type (Monthly 30-second / Annual 90-minute) | ________________________________________________ |
| Weather / ambient conditions | ________________________________________________ |

Unit identification and location

| Field | Entry |
| --- | --- |
| Unit ID / asset number | ________________________________________________ |
| Location (building, floor, room, zone) | ________________________________________________ |
| Fixture type (exit sign, egress light, combination unit) | ________________________________________________ |
| Battery type and install date | ________________________________________________ |

Monthly functional test (30-second)

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Visual inspection: physical damage, loose mounting, blocked light path, clear lens | ☐ | ☐ | ☐ | ____________________ |
| Test button activated – light illuminates within 10 seconds | ☐ | ☐ | ☐ | ____________________ |
| Light remains on without flickering for full 30 seconds | ☐ | ☐ | ☐ | ____________________ |
| Result: Pass / Fail (with defect description if Fail) | ☐ | ☐ | ☐ | ____________________ |

Annual full-duration test (90-minute)

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Power supply disconnected (simulated power failure) | ☐ | ☐ | ☐ | ____________________ |
| Light illuminates within 10 seconds | ☐ | ☐ | ☐ | ____________________ |
| Illumination maintained for full 90 minutes | ☐ | ☐ | ☐ | ____________________ |
| Illumination level: average ≥ 1 foot-candle (10.8 lux) at floor level along egress path | ☐ | ☐ | ☐ | ____________________ |
| Result: Pass / Fail | ☐ | ☐ | ☐ | ____________________ |

Corrective action and sign-off

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Failed units: specific defect noted | ☐ | ☐ | ☐ | ____________________ |
| Corrective action assigned (repair / replace / electrician call) | ☐ | ☐ | ☐ | ____________________ |
| Target repair date | ☐ | ☐ | ☐ | ____________________ |
| Inspector signature and date | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________

References consulted

NFPA 101: Life Safety Code, §7.9 Emergency Lighting (2024)

OSHA 29 CFR 1910.37 – Exit routes

NFPA 101 §7.9.3 – Testing and maintenance

UL 924 – Standard for Emergency Lighting and Power Equipment

Verify the current edition and local adoption before use.