InspectionReport
Hot Work Permit and Fire Watch Checklist
Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.
Jurisdiction: Adaptable. Covers OSHA 29 CFR 1910.252 (US General Industry) and 1926.352 (US Construction), NFPA 51B, and UK HSE hot work requirements. Adaptable to other jurisdictions. Apply only the section and thresholds for the governing jurisdiction; do not combine US and UK requirements as if they were one code.
	Site / Project: ______________________________
	Address: ______________________________

	Inspector name: ______________________________
	Company: ______________________________

	Date: ______________________________
	Time: ______________________________


Inspection checklist
Permit header
	Field
	Entry

	Permit number
	________________________________________________

	Date and time of issue
	________________________________________________

	Location of hot work
	________________________________________________

	Type of hot work (welding, cutting, grinding, brazing)
	________________________________________________

	Permit issuer name and signature
	________________________________________________


Hot work zone preparation
	Item
	Pass
	Fail
	N/A
	Notes

	Movable combustibles: all relocated 35 feet (10 meters) from hot work
	☐
	☐
	☐
	____________________

	Immovable combustibles: protected by approved fire-resistant blankets, curtains, or metal shields
	☐
	☐
	☐
	____________________

	Floor and wall openings: wet down or covered with damp sand / fire-resistant shields
	☐
	☐
	☐
	____________________

	Cracks in walls, doorways, open pipes within 35-foot zone: sealed
	☐
	☐
	☐
	____________________


Atmospheric testing
	Item
	Pass
	Fail
	N/A
	Notes

	Flammable vapors / dust: below 10% LEL
	☐
	☐
	☐
	____________________

	Confined space: continuous mechanical ventilation and atmospheric gas monitoring
	☐
	☐
	☐
	____________________

	Empty drums / tanks: verified of flammable vapor residues
	☐
	☐
	☐
	____________________

	Wheels with inflated tires: not subjected to heat
	☐
	☐
	☐
	____________________


Fire watch assignment
	Item
	Pass
	Fail
	N/A
	Notes

	Fire watch person assigned: name
	☐
	☐
	☐
	____________________

	Sole responsibility (no other duties during hot work)
	☐
	☐
	☐
	____________________

	Authority to stop work if hazardous conditions develop
	☐
	☐
	☐
	____________________

	Equipment: fully charged fire extinguisher (appropriate type) and direct communication (radio / alarm)
	☐
	☐
	☐
	____________________


Post-work fire watch duration
	Item
	Pass
	Fail
	N/A
	Notes

	Minimum duration: 30 minutes (OSHA) / 60 minutes (NFPA 51B / insurers)
	☐
	☐
	☐
	____________________

	High-risk environments: up to 3 hours (dense concealed combustibles)
	☐
	☐
	☐
	____________________

	Continuous monitoring for first 30 minutes, then intermittent inspection
	☐
	☐
	☐
	____________________

	Final inspection by permit issuer: area normalized
	☐
	☐
	☐
	____________________


Permit closure
	Item
	Pass
	Fail
	N/A
	Notes

	Post-work monitoring period completed without incident
	☐
	☐
	☐
	____________________

	Final inspection conducted
	☐
	☐
	☐
	____________________

	Permit closed by permit issuer
	☐
	☐
	☐
	____________________

	Time of permit closure
	☐
	☐
	☐
	____________________

	Permit issuer signature
	☐
	☐
	☐
	____________________


Findings
	#
	Item
	Location
	Severity
	Action required

	1
	
	
	
	

	2
	
	
	
	

	3
	
	
	
	

	4
	
	
	
	

	5
	
	
	
	

	6
	
	
	
	

	7
	
	
	
	

	8
	
	
	
	


Signature
Inspector signature: ______________________________    Name: ______________________________
Date: ______________________________
References consulted
OSHA 29 CFR 1910.252 – Welding, cutting, and heating
OSHA 29 CFR 1926.352 – Welding, cutting, and heating (construction)
NFPA 51B: Standard for Fire Prevention During Welding, Cutting, and Other Hot Work (2021)
UK HSE – Hot work permit systems
Verify the current edition and local adoption before use.
Free resource from inspectionreport.app - build an evidence-backed report from photos at https://www.inspectionreport.app/new-report
