InspectionReport

Healthcare ICRA Compliance Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

Negative Air System Integrity

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify HEPA filter on Negative Air Machine (NAM) is properly sealed and undamaged. Visually inspect the filter and housing for any gaps or tears. | ☐ | ☐ | ☐ | ____________________ |
| Confirm NAM airflow rate meets or exceeds the required air changes per hour (ACH) for the contained area, as specified in the ICRA plan. Document readings. | ☐ | ☐ | ☐ | ____________________ |
| Measure and record negative pressure differential between the contained area and adjacent spaces. Ensure a minimum of -0.01 inches of water column (WC) is maintained. | ☐ | ☐ | ☐ | ____________________ |
| Ensure NAM exhaust is directed outside the building or to a location away from air intakes and pedestrian traffic. Verify exhaust is not recirculating within the facility. | ☐ | ☐ | ☐ | ____________________ |
| Verify NAM is connected to a reliable power source, preferably a backup generator circuit. Check for any loose connections or damaged cords. | ☐ | ☐ | ☐ | ____________________ |
| Inspect NAM pre-filter for excessive dust accumulation. Replace or clean the pre-filter as needed to maintain optimal airflow. | ☐ | ☐ | ☐ | ____________________ |
| Confirm NAM operation log is maintained, documenting daily readings, filter changes, and any maintenance performed. | ☐ | ☐ | ☐ | ____________________ |
| If equipped, test the NAM alarm system to ensure it functions correctly and alerts personnel to pressure loss or equipment failure. | ☐ | ☐ | ☐ | ____________________ |
| Verify the NAM's calibration date is current. Schedule recalibration as needed per manufacturer's recommendations. | ☐ | ☐ | ☐ | ____________________ |
| Assess NAM noise levels to ensure they do not exceed acceptable limits for patient care areas. Implement noise reduction measures if necessary. | ☐ | ☐ | ☐ | ____________________ |

Dust Partition and Barrier Integrity

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Inspect all seams and joints of the dust partition for complete sealing. Use tape or sealant to close any gaps or openings. | ☐ | ☐ | ☐ | ____________________ |
| Verify the barrier material (e.g., polyethylene sheeting) is intact and free from tears, punctures, or damage. Repair or replace damaged sections immediately. | ☐ | ☐ | ☐ | ____________________ |
| Confirm the ante-room is properly configured with appropriate airlocks and signage. Ensure personnel are using the ante-room for entry and exit. | ☐ | ☐ | ☐ | ____________________ |
| Inspect all ductwork within the contained area for proper sealing. Seal any leaks or gaps with appropriate tape or sealant to prevent dust migration. | ☐ | ☐ | ☐ | ____________________ |
| If a pass-through is used, verify it is properly sealed and maintained to prevent dust migration. Ensure doors or covers are tightly closed when not in use. | ☐ | ☐ | ☐ | ____________________ |
| Check that the barrier is securely anchored to the walls, floor, and ceiling. Ensure the anchoring method is appropriate for the surface material. | ☐ | ☐ | ☐ | ____________________ |
| Verify appropriate ICRA signage is prominently displayed at all entrances to the contained area, warning of potential hazards and required PPE. | ☐ | ☐ | ☐ | ____________________ |
| Assess the overall stability of the barrier. Ensure it can withstand normal traffic and environmental conditions without collapsing or shifting. | ☐ | ☐ | ☐ | ____________________ |
| Confirm the barrier material meets fire resistance requirements, if applicable. Use fire-retardant materials in accordance with local codes. | ☐ | ☐ | ☐ | ____________________ |
| Ensure all access points to the contained area are clearly marked and controlled. Limit access to authorized personnel only. | ☐ | ☐ | ☐ | ____________________ |

Personnel and Material Management

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify sticky mats are in place at all entrances to the contained area and are being replaced regularly when soiled. Check for proper disposal procedures. | ☐ | ☐ | ☐ | ____________________ |
| Confirm appropriate PPE (e.g., respirators, gloves, gowns) is readily available and being used by all personnel entering the contained area. | ☐ | ☐ | ☐ | ____________________ |
| Ensure hand hygiene stations (e.g., hand sanitizer dispensers) are readily accessible at all entrances and exits to the contained area. | ☐ | ☐ | ☐ | ____________________ |
| Verify tools and equipment are being cleaned and disinfected before being removed from the contained area. Check for appropriate cleaning agents. | ☐ | ☐ | ☐ | ____________________ |
| Confirm waste disposal procedures are being followed, including proper segregation, labeling, and containment of potentially contaminated materials. | ☐ | ☐ | ☐ | ____________________ |
| Review personnel training records to ensure all workers have received adequate ICRA training and understand the required protocols. | ☐ | ☐ | ☐ | ____________________ |
| If a material tracking system is in place, verify it is being used to track the movement of materials in and out of the contained area. | ☐ | ☐ | ☐ | ____________________ |
| Ensure equipment and materials are stored properly within the contained area to minimize dust generation and maintain a clean work environment. | ☐ | ☐ | ☐ | ____________________ |
| Implement controls to limit visitor access to the contained area. Ensure visitors are informed of the required safety protocols and PPE. | ☐ | ☐ | ☐ | ____________________ |
| Verify emergency procedures are in place and communicated to all personnel, including evacuation routes and contact information. | ☐ | ☐ | ☐ | ____________________ |

Documentation and Communication

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Confirm the ICRA plan is readily available on-site and accessible to all personnel involved in the renovation project. | ☐ | ☐ | ☐ | ____________________ |
| Verify the daily ICRA checklist is being completed and signed by a designated person. Review completed checklists for any identified issues. | ☐ | ☐ | ☐ | ____________________ |
| Ensure communication protocols are in place to inform hospital staff and patients about the renovation project and any potential disruptions. | ☐ | ☐ | ☐ | ____________________ |
| Verify an incident reporting system is in place to document any ICRA-related incidents or near misses. Ensure incidents are investigated and corrective actions are implemented. | ☐ | ☐ | ☐ | ____________________ |
| Confirm contact information for key personnel (e.g., infection control officer, project manager) is readily available and up-to-date. | ☐ | ☐ | ☐ | ____________________ |
| If a permit-to-work system is in place, verify all required permits are obtained before starting any renovation work. | ☐ | ☐ | ☐ | ____________________ |
| Ensure a change management process is in place to address any changes to the ICRA plan or renovation project. Document all changes and communicate them to relevant personnel. | ☐ | ☐ | ☐ | ____________________ |
| Review meeting minutes to ensure ICRA-related issues are being discussed and addressed in a timely manner. | ☐ | ☐ | ☐ | ____________________ |
| Verify all required regulatory compliance documentation (e.g., permits, licenses) is readily available and up-to-date. | ☐ | ☐ | ☐ | ____________________ |
| Confirm the schedule for ICRA audits and inspections is being followed. Review audit reports for any identified deficiencies. | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________