InspectionReport

Hydrostatic Pressure Testing Safety Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

Pre-Test Planning & Documentation

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Has a written hydrostatic test plan been reviewed and approved by a qualified engineer or the Authority Having Jurisdiction (AHJ)? | ☐ | ☐ | ☐ | ____________________ |
| Is the specified test pressure clearly documented and does it NOT exceed the maximum allowable test pressure for the piping system and components (typically 1.5 times the design pressure)? | ☐ | ☐ | ☐ | ____________________ |
| Has material compatibility with the test fluid (typically potable water) been verified for all piping components, including gaskets and seals? | ☐ | ☐ | ☐ | ____________________ |
| Are all isolation valves that will be subjected to test pressure rated for that pressure and in good working order? | ☐ | ☐ | ☐ | ____________________ |
| Is the pressure gauge calibrated and certified within the last year? Verify calibration sticker is present and legible. | ☐ | ☐ | ☐ | ____________________ |
| Is there a documented procedure for venting trapped air from the system during filling? | ☐ | ☐ | ☐ | ____________________ |
| Is there a documented procedure for safely draining the system after the test? | ☐ | ☐ | ☐ | ____________________ |
| Is there an emergency plan in place in case of a pipe rupture or other failure during the test? | ☐ | ☐ | ☐ | ____________________ |

Piping System Preparation

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Are all pipe supports and hangers properly installed and capable of supporting the weight of the water-filled piping system? | ☐ | ☐ | ☐ | ____________________ |
| Are adequate thrust blocks or other restraints installed at all dead ends, tees, and bends to prevent movement due to hydrostatic pressure? Verify design calculations. | ☐ | ☐ | ☐ | ____________________ |
| Are all test caps and plugs rated for at least the specified test pressure? Verify markings are present and legible. | ☐ | ☐ | ☐ | ____________________ |
| Are test caps securely installed with appropriate thread sealant or gaskets to prevent leaks or blowouts? | ☐ | ☐ | ☐ | ____________________ |
| Are all valves within the test section in the fully open or fully closed position as required by the test plan? | ☐ | ☐ | ☐ | ____________________ |
| Has the piping system been flushed to remove debris and contaminants prior to testing? | ☐ | ☐ | ☐ | ____________________ |
| Are temporary supports installed as needed to prevent sagging or overstressing of the piping during testing? | ☐ | ☐ | ☐ | ____________________ |
| Are expansion joints properly restrained or isolated during the test to prevent damage? | ☐ | ☐ | ☐ | ____________________ |

Exclusion Zone & Personnel Safety

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Has a clearly marked exclusion zone been established around the piping system during the test? Minimum radius: 25 feet. | ☐ | ☐ | ☐ | ____________________ |
| Have all non-essential personnel been evacuated from the exclusion zone? | ☐ | ☐ | ☐ | ____________________ |
| Are warning signs posted at the perimeter of the exclusion zone indicating the presence of a hydrostatic pressure test? | ☐ | ☐ | ☐ | ____________________ |
| Are all personnel involved in the test wearing appropriate PPE, including safety glasses, hard hats, and steel-toed boots? | ☐ | ☐ | ☐ | ____________________ |
| Is there a reliable communication system in place to allow personnel to communicate during the test? | ☐ | ☐ | ☐ | ____________________ |
| Is there a readily accessible emergency shutdown valve or other means of quickly depressurizing the system in case of a failure? | ☐ | ☐ | ☐ | ____________________ |
| Verify that PNEUMATIC (air) testing is ABSOLUTELY PROHIBITED on PVC or other plastic piping systems. Only hydrostatic testing is permitted. | ☐ | ☐ | ☐ | ____________________ |
| During pressurization, are personnel visually monitoring the piping system from a safe distance for any signs of leaks or distress? | ☐ | ☐ | ☐ | ____________________ |

Test Execution & Monitoring

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Is the system being pressurized slowly and in a controlled manner to prevent pressure surges? | ☐ | ☐ | ☐ | ____________________ |
| Is the pressure being continuously monitored during the test using a calibrated pressure gauge? | ☐ | ☐ | ☐ | ____________________ |
| Is the system being visually inspected for leaks at all joints, connections, and fittings? | ☐ | ☐ | ☐ | ____________________ |
| Is the pressure drop being monitored over the duration of the test to ensure it remains within acceptable limits (typically less than 5% of the test pressure)? | ☐ | ☐ | ☐ | ____________________ |
| Is the system being held at the specified test pressure for the required duration (typically 2-4 hours)? | ☐ | ☐ | ☐ | ____________________ |
| If leaks are detected, is there a procedure in place for safely depressurizing the system and repairing the leaks? | ☐ | ☐ | ☐ | ____________________ |
| After repairs, is the system being retested to verify the integrity of the repairs? | ☐ | ☐ | ☐ | ____________________ |
| Is the water temperature being monitored during the test to account for thermal expansion or contraction? | ☐ | ☐ | ☐ | ____________________ |
| Is a properly sized pressure relief valve installed to prevent over-pressurization of the system? | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________