InspectionReport

Monthly Portable Fire Extinguisher Inspection Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

Accessibility and Placement

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Is the fire extinguisher located in its designated place, as indicated on the fire safety plan? | ☐ | ☐ | ☐ | ____________________ |
| Is the fire extinguisher readily accessible and unobstructed? Ensure a minimum clearance of 3 feet around the extinguisher. | ☐ | ☐ | ☐ | ____________________ |
| Is the fire extinguisher visible and not hidden behind objects or in obscured locations? | ☐ | ☐ | ☐ | ____________________ |
| Is the fire extinguisher mounted at the correct height? The top of the extinguisher should be no more than 5 feet above the floor for extinguishers weighing less than 40 lbs. | ☐ | ☐ | ☐ | ____________________ |
| Is there appropriate signage indicating the location and type (Class ABC) of the fire extinguisher? | ☐ | ☐ | ☐ | ____________________ |
| Is the fire extinguisher protected from environmental conditions (e.g., excessive heat, cold, moisture) that could affect its operation? | ☐ | ☐ | ☐ | ____________________ |
| Is the fire extinguisher the correct type (Class ABC) for the potential fire hazards in the area? | ☐ | ☐ | ☐ | ____________________ |
| Is the number of fire extinguishers adequate for the size and occupancy of the area? | ☐ | ☐ | ☐ | ____________________ |
| Is the bottom of the extinguisher at least 4 inches off the floor? | ☐ | ☐ | ☐ | ____________________ |

Physical Condition

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Inspect the extinguisher for any signs of physical damage, such as dents, corrosion, or leakage. | ☐ | ☐ | ☐ | ____________________ |
| Check the hose and nozzle for cracks, blockages, or damage. Ensure the nozzle is securely attached. | ☐ | ☐ | ☐ | ____________________ |
| Ensure the handle and lever are in good working order and not damaged or corroded. | ☐ | ☐ | ☐ | ____________________ |
| Inspect the extinguisher shell for any signs of rust, corrosion, or other deterioration. | ☐ | ☐ | ☐ | ____________________ |
| Is the extinguisher clean and free from dust, dirt, or other contaminants? | ☐ | ☐ | ☐ | ____________________ |
| Are the operating instructions clearly legible and facing outward? | ☐ | ☐ | ☐ | ____________________ |
| Does the extinguisher feel approximately full by lifting it? Note any significant weight difference. | ☐ | ☐ | ☐ | ____________________ |
| Are all labels and markings legible and securely attached? | ☐ | ☐ | ☐ | ____________________ |

Pressure and Seals

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify the pressure gauge is within the operable range (green zone). Note any extinguishers with low or high pressure. | ☐ | ☐ | ☐ | ____________________ |
| Is the tamper seal intact and unbroken? If broken, the extinguisher may have been used or tampered with. | ☐ | ☐ | ☐ | ____________________ |
| Is the locking pin securely in place and easily removable in case of emergency? | ☐ | ☐ | ☐ | ____________________ |
| Ensure the discharge valve is free from obstructions and operates smoothly. | ☐ | ☐ | ☐ | ____________________ |
| If applicable, check the regulator for proper function and settings. | ☐ | ☐ | ☐ | ____________________ |
| For cartridge-operated extinguishers, verify the cartridge is properly installed and not punctured. | ☐ | ☐ | ☐ | ____________________ |

Inspection and Maintenance Records

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Is the monthly inspection tag attached and properly filled out with the date and initials of the inspector? | ☐ | ☐ | ☐ | ____________________ |
| Verify the extinguisher has undergone an annual inspection within the past year, as indicated on the inspection tag. | ☐ | ☐ | ☐ | ____________________ |
| Check the hydrostatic test date. Ensure the extinguisher is within its required hydrostatic test interval (typically every 5 or 12 years, depending on the type). | ☐ | ☐ | ☐ | ____________________ |
| Review maintenance records to ensure any necessary repairs or servicing has been performed. | ☐ | ☐ | ☐ | ____________________ |
| If the extinguisher has been discharged, verify the recharge date and ensure it was performed by a qualified technician. | ☐ | ☐ | ☐ | ____________________ |
| Confirm the extinguisher's location matches the facility's fire safety plan and extinguisher location map. | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________