InspectionReport

Sewer Bypass Pumping Setup Inspection Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

HDPE Fusion Welds & Piping

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Visually inspect all HDPE fusion welds for complete bead formation and absence of cracks or voids. (ASTM F2620) | ☐ | ☐ | ☐ | ____________________ |
| Verify that all newly fused HDPE joints have passed the required pressure test (typically 1.5 times operating pressure for 2 hours). Document test results. | ☐ | ☐ | ☐ | ____________________ |
| Confirm that HDPE pipe supports are spaced according to the manufacturer's recommendations (typically 8-10 feet for larger diameter pipe) to prevent sagging and stress on joints. | ☐ | ☐ | ☐ | ____________________ |
| Check that the bypass piping is adequately anchored to prevent movement due to hydraulic forces, especially at bends and connections. | ☐ | ☐ | ☐ | ____________________ |
| Inspect all pipe joints and connections for leaks. Address any leaks immediately to prevent spills and environmental contamination. | ☐ | ☐ | ☐ | ____________________ |
| Verify proper bedding (sand or gravel) under the HDPE pipe to prevent damage from rocks or uneven surfaces. (AWWA M55) | ☐ | ☐ | ☐ | ____________________ |
| Confirm that the HDPE fusion machine is calibrated per manufacturer's specifications and calibration records are available. | ☐ | ☐ | ☐ | ____________________ |
| Ensure that all bypass piping is clearly labeled with flow direction and contents (e.g., 'Raw Sewage Bypass'). | ☐ | ☐ | ☐ | ____________________ |
| Assess if the bypass piping is adequately protected from vehicular traffic or other potential damage sources (e.g., barriers, signage). | ☐ | ☐ | ☐ | ____________________ |
| Check for adequate expansion loops or flexible couplings to accommodate thermal expansion and contraction of the HDPE pipe. | ☐ | ☐ | ☐ | ____________________ |

Bypass Pump Operation & Monitoring

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Measure and record the suction lift of each bypass pump. Ensure it is within the pump manufacturer's recommended limits to prevent cavitation. | ☐ | ☐ | ☐ | ____________________ |
| Monitor and record the discharge pressure of each bypass pump. Note any significant fluctuations that could indicate a problem. | ☐ | ☐ | ☐ | ____________________ |
| Measure and record the flow rate of each bypass pump. Compare to the required flow rate to ensure adequate bypass capacity. | ☐ | ☐ | ☐ | ____________________ |
| Verify that each bypass pump has adequate secondary containment (e.g., lined berm) to contain any spills or leaks. | ☐ | ☐ | ☐ | ____________________ |
| Check the fuel level of each bypass pump and ensure an adequate supply for continuous operation. Document fuel levels. | ☐ | ☐ | ☐ | ____________________ |
| Check the oil level of each bypass pump and add oil as needed. Document oil levels. | ☐ | ☐ | ☐ | ____________________ |
| Listen for unusual noises or vibrations from each bypass pump. Investigate and correct any issues promptly. | ☐ | ☐ | ☐ | ____________________ |
| If equipped, test the automatic start/stop function of the bypass pumps to ensure proper operation in case of power failure or high-level alarm. | ☐ | ☐ | ☐ | ____________________ |
| Inspect the pump suction screen for debris buildup and clean as needed to prevent pump cavitation and reduced flow. | ☐ | ☐ | ☐ | ____________________ |
| Record the operating hours of each pump daily. Use this data for preventative maintenance scheduling. | ☐ | ☐ | ☐ | ____________________ |
| Inspect the area around the pump discharge for erosion or washouts. Implement erosion control measures as needed. | ☐ | ☐ | ☐ | ____________________ |

Manhole Entry & Confined Space Procedures

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify that a valid confined space entry permit is in place before any manhole entry. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Test the atmosphere in the manhole for oxygen levels (19.5-23.5%), flammable gases (less than 10% LEL), and toxic gases (H2S, CO) before entry and continuously during occupancy. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Ensure that the manhole is adequately ventilated with a blower to remove hazardous atmospheres. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Confirm that a trained attendant is stationed outside the manhole to monitor entrants and provide assistance if needed. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Verify that appropriate rescue equipment (harness, lifeline, retrieval device) is available and in good working order at the manhole entry point. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Ensure that fall protection measures (e.g., manhole guardrail, safety net) are in place to prevent falls into the manhole. (OSHA 1926.501) | ☐ | ☐ | ☐ | ____________________ |
| Establish a clear communication system (e.g., two-way radio) between the entrant and the attendant. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Provide adequate lighting at the manhole entry point and inside the manhole. (OSHA 1910.146) | ☐ | ☐ | ☐ | ____________________ |
| Ensure that the manhole is properly barricaded to prevent unauthorized access. (OSHA 1926.200) | ☐ | ☐ | ☐ | ____________________ |
| Verify that the gas monitor used for atmospheric testing is calibrated and bump tested daily. (Manufacturer Specs) | ☐ | ☐ | ☐ | ____________________ |
| Implement Lockout/Tagout procedures for any equipment that could pose a hazard to entrants (e.g., upstream pumps). (OSHA 1910.147) | ☐ | ☐ | ☐ | ____________________ |

Site Conditions & General Safety

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Maintain a clean and organized work area to prevent trips, slips, and falls. (OSHA 1926.25) | ☐ | ☐ | ☐ | ____________________ |
| Implement erosion control measures to prevent soil erosion and sedimentation of waterways. (EPA Regulations) | ☐ | ☐ | ☐ | ____________________ |
| Establish a traffic control plan to protect workers from vehicular traffic. (MUTCD) | ☐ | ☐ | ☐ | ____________________ |
| Provide adequate lighting for all work areas, especially during nighttime operations. (OSHA 1926.56) | ☐ | ☐ | ☐ | ____________________ |
| Review the site-specific emergency response plan with all personnel. (OSHA 1910.38) | ☐ | ☐ | ☐ | ____________________ |
| Ensure that a first-aid kit is readily available and adequately stocked. (ANSI Z308.1) | ☐ | ☐ | ☐ | ____________________ |
| Verify that fire extinguishers are readily accessible and inspected monthly. (NFPA 10) | ☐ | ☐ | ☐ | ____________________ |
| Establish a reliable communication system (e.g., two-way radios, cell phones) for all personnel. (Best Practice) | ☐ | ☐ | ☐ | ____________________ |
| Implement security measures to prevent unauthorized access to the site. (Best Practice) | ☐ | ☐ | ☐ | ____________________ |
| Monitor weather conditions and adjust work activities as needed to ensure safety. (Best Practice) | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________