InspectionReport

High-Voltage Switchgear Installation Safety Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

I. Pre-Installation Site Assessment

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Is site access controlled and restricted to authorized personnel only? (Lockout/Tagout procedures in place) | ☐ | ☐ | ☐ | ____________________ |
| Has a soil resistivity test been performed to determine appropriate grounding requirements per IEEE 80? | ☐ | ☐ | ☐ | ____________________ |
| Have all underground utilities been located and marked before excavation (One-Call system)? | ☐ | ☐ | ☐ | ____________________ |
| Are weather conditions (wind, rain, temperature) suitable for safe high-voltage work? (Refer to company policy). | ☐ | ☐ | ☐ | ____________________ |
| Is the switchgear staging area clear of obstructions and properly graded to prevent water accumulation? | ☐ | ☐ | ☐ | ____________________ |
| Is the site-specific emergency response plan documented, communicated, and readily available? | ☐ | ☐ | ☐ | ____________________ |
| Is a reliable communication system (e.g., two-way radios) available for all personnel? | ☐ | ☐ | ☐ | ____________________ |
| Are adequate first aid supplies and trained personnel available on site? | ☐ | ☐ | ☐ | ____________________ |
| Has an arc flash hazard analysis been completed for the specific switchgear configuration? | ☐ | ☐ | ☐ | ____________________ |
| Are all personnel involved in the installation qualified and trained for high-voltage work? | ☐ | ☐ | ☐ | ____________________ |

II. Grounding and Bonding

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Is the grounding electrode system installed per NEC 250, including grounding rods, ground ring, and connections to the switchgear? | ☐ | ☐ | ☐ | ____________________ |
| Are grounding rods driven to a depth of at least 8 feet (2.44 m) and spaced at least 6 feet (1.83 m) apart? | ☐ | ☐ | ☐ | ____________________ |
| Are grounding conductors sized appropriately per NEC 250.66 based on the size of the service entrance conductors? | ☐ | ☐ | ☐ | ____________________ |
| Are equipment grounding conductors (EGCs) properly installed and connected to all metallic enclosures and non-current-carrying parts? | ☐ | ☐ | ☐ | ____________________ |
| Are bonding jumpers installed around all expansion joints, flexible metal conduit, and other discontinuities in the grounding path? | ☐ | ☐ | ☐ | ____________________ |
| Has a ground resistance test been performed to verify that the grounding system meets the required impedance levels (typically < 25 ohms)? | ☐ | ☐ | ☐ | ____________________ |
| Have step and touch potential calculations been performed, and are mitigation measures (e.g., ground grid, equipotential plane) in place? | ☐ | ☐ | ☐ | ____________________ |
| Is the DC system grounding configuration compliant with NEC 690, including proper grounding of the DC combiner boxes and inverters? | ☐ | ☐ | ☐ | ____________________ |
| Are surge protection devices (SPDs) installed on both the AC and DC sides of the switchgear to protect against voltage transients? | ☐ | ☐ | ☐ | ____________________ |
| Are all grounding connections clean, tight, and free of corrosion? (Use anti-oxidant compound). | ☐ | ☐ | ☐ | ____________________ |

III. Switchgear Installation and Commissioning

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Is the switchgear securely anchored to the concrete pad per the manufacturer's specifications? | ☐ | ☐ | ☐ | ____________________ |
| Are all cable terminations properly torqued and insulated per the manufacturer's instructions and applicable standards? | ☐ | ☐ | ☐ | ____________________ |
| Are all cables clearly labeled with their voltage, phase, and destination? | ☐ | ☐ | ☐ | ____________________ |
| Has an insulation resistance test (megger test) been performed on all cables before energization? | ☐ | ☐ | ☐ | ____________________ |
| Is a voltage test performed to verify correct voltage levels and phase rotation before connecting to the grid? | ☐ | ☐ | ☐ | ____________________ |
| Are all protective relays (e.g., overcurrent, overvoltage) properly set and tested? | ☐ | ☐ | ☐ | ____________________ |
| Is all control wiring properly connected and tested for functionality? | ☐ | ☐ | ☐ | ____________________ |
| Does the switchgear nameplate match the system design and specifications? | ☐ | ☐ | ☐ | ____________________ |
| Is the switchgear ventilation and cooling system functioning correctly to prevent overheating? | ☐ | ☐ | ☐ | ____________________ |
| Are arc flash mitigation measures (e.g., arc flash relays, current limiting fuses) properly installed and tested? | ☐ | ☐ | ☐ | ____________________ |
| Are the inverters compatible with the switchgear's voltage and current ratings? | ☐ | ☐ | ☐ | ____________________ |

IV. Personal Protective Equipment (PPE) and Safety Procedures

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Are all personnel wearing appropriate arc-rated clothing (e.g., shirts, pants, suits) based on the arc flash hazard analysis? | ☐ | ☐ | ☐ | ____________________ |
| Are voltage-rated gloves being used, inspected before each use, and properly stored? | ☐ | ☐ | ☐ | ____________________ |
| Are safety glasses with side shields or a face shield being worn for eye protection? | ☐ | ☐ | ☐ | ____________________ |
| Are insulated tools being used for all work within the arc flash boundary? | ☐ | ☐ | ☐ | ____________________ |
| Is a hot work permit required and obtained before performing any work that could create an ignition source? | ☐ | ☐ | ☐ | ____________________ |
| Are proper Lockout/Tagout (LOTO) procedures being followed to de-energize and isolate the switchgear before any work is performed? | ☐ | ☐ | ☐ | ____________________ |
| Is rubber matting or other insulating material used to provide additional protection from step and touch potential? | ☐ | ☐ | ☐ | ____________________ |
| Is a qualified safety observer present during all high-voltage work? | ☐ | ☐ | ☐ | ____________________ |
| Is an insulated rescue hook readily available in case of an electrical emergency? | ☐ | ☐ | ☐ | ____________________ |
| Is a calibrated voltage detector used to verify that equipment is de-energized before starting work? | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________