InspectionReport

Utility Pole Transformer Installation Safety Checklist

Documentation aid only. Adapt this resource to the site, manufacturer instructions, and applicable local requirements. It does not replace a competent person, professional judgment, legal advice, or a required statutory form.

| Site / Project: ______________________________ | Address: ______________________________ |
| --- | --- |
| Inspector name: ______________________________ | Company: ______________________________ |
| Date: ______________________________ | Time: ______________________________ |

Inspection checklist

Pre-Climb Pole Inspection & Preparation

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Perform pole sounding test around the base of the pole to identify decay or weakness. Document results. | ☐ | ☐ | ☐ | ____________________ |
| Visually inspect the pole for cracks, splits, woodpecker damage, or other signs of deterioration above and below the climbing area. | ☐ | ☐ | ☐ | ____________________ |
| Verify bucket truck grounding using a grounding clamp connected to a driven ground rod. Test ground resistance (target <25 ohms). | ☐ | ☐ | ☐ | ____________________ |
| Assess the existing load on the pole and ensure it can safely support the additional weight of the transformer and personnel. Consult engineering if unsure. | ☐ | ☐ | ☐ | ____________________ |
| Identify and address any foreign attachments (e.g., unauthorized communication lines) that could interfere with the installation. | ☐ | ☐ | ☐ | ____________________ |
| Establish a clear work zone around the pole using barricades, cones, and warning signs to protect the public. | ☐ | ☐ | ☐ | ____________________ |
| Evaluate weather conditions (wind, rain, lightning) and postpone work if conditions are unsafe. Follow company policy on weather-related work stoppages. | ☐ | ☐ | ☐ | ____________________ |
| Confirm a clear communication plan is in place between all crew members, including hand signals and radio protocols. | ☐ | ☐ | ☐ | ____________________ |
| Verify the integrity of the fall arrest anchor point on the pole before commencing work. Ensure it meets load requirements. | ☐ | ☐ | ☐ | ____________________ |
| Inspect the pole ground sleeve for corrosion and proper connection to the grounding system. | ☐ | ☐ | ☐ | ____________________ |

Personal Protective Equipment (PPE)

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Inspect rubber insulating gloves for damage (cuts, punctures, air leaks) before each use. Perform air test. Ensure proper voltage rating. | ☐ | ☐ | ☐ | ____________________ |
| Wear leather glove protectors over rubber insulating gloves to prevent physical damage. | ☐ | ☐ | ☐ | ____________________ |
| Inspect lineman's belt and safety strap for cuts, abrasions, or defects. Ensure proper fit and functionality. | ☐ | ☐ | ☐ | ____________________ |
| Verify hard hat is in good condition (no cracks, dents) and meets ANSI Z89.1 standards. Chin strap must be used. | ☐ | ☐ | ☐ | ____________________ |
| Wear safety glasses or face shield to protect eyes from debris and arc flash hazards. | ☐ | ☐ | ☐ | ____________________ |
| Wear flame-resistant (FR) clothing that meets NFPA 70E requirements. Ensure proper arc rating. | ☐ | ☐ | ☐ | ____________________ |
| Wear EH-rated (Electrical Hazard) insulating boots with proper ankle support. | ☐ | ☐ | ☐ | ____________________ |
| Avoid wearing loose clothing or jewelry that could snag on equipment or conduct electricity. | ☐ | ☐ | ☐ | ____________________ |
| Inspect hot sticks for cleanliness, cracks, and proper dielectric strength before each use. Verify voltage rating. | ☐ | ☐ | ☐ | ____________________ |
| Inspect insulating blankets and line hose for damage and cleanliness. Ensure proper voltage rating. | ☐ | ☐ | ☐ | ____________________ |

Transformer Handling & PCB Awareness

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify the transformer is properly labeled for PCB content. If PCB-containing, follow specific handling procedures. | ☐ | ☐ | ☐ | ____________________ |
| Ensure spill containment materials (absorbent pads, booms) are readily available in case of transformer oil leaks. | ☐ | ☐ | ☐ | ____________________ |
| Inspect lifting equipment (slings, chains, hoists) for damage and proper load rating before lifting the transformer. | ☐ | ☐ | ☐ | ____________________ |
| Develop a detailed lifting plan that considers the weight of the transformer, lifting angles, and potential obstructions. | ☐ | ☐ | ☐ | ____________________ |
| Ensure a qualified rigger supervises the transformer lifting operation. | ☐ | ☐ | ☐ | ____________________ |
| Visually inspect the transformer for any signs of damage (leaks, cracks) before installation. | ☐ | ☐ | ☐ | ____________________ |
| Confirm proper disposal procedures are in place for any PCB-contaminated materials (rags, soil). | ☐ | ☐ | ☐ | ____________________ |
| Verify all personnel involved in the installation have received adequate training on PCB hazards and handling procedures. | ☐ | ☐ | ☐ | ____________________ |
| Ensure the transformer is securely mounted to the pole using appropriate hardware and brackets. | ☐ | ☐ | ☐ | ____________________ |
| Inspect all hardware (bolts, nuts, washers) for proper size, material, and condition before use. | ☐ | ☐ | ☐ | ____________________ |

Electrical Safety & Hot Work Practices

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Verify the primary conductors are de-energized and properly grounded before commencing work. Use a voltage tester to confirm. | ☐ | ☐ | ☐ | ____________________ |
| Use insulating cover-up (blankets, line hose) on adjacent energized conductors to prevent accidental contact. | ☐ | ☐ | ☐ | ____________________ |
| Maintain the required minimum approach distance from energized conductors based on voltage level. Consult the MAD chart. | ☐ | ☐ | ☐ | ____________________ |
| Use proper hot stick techniques when working on or near energized conductors. Ensure smooth, controlled movements. | ☐ | ☐ | ☐ | ____________________ |
| Follow established grounding procedures to protect against accidental energization. Use properly sized grounding cables and clamps. | ☐ | ☐ | ☐ | ____________________ |
| Conduct an arc flash hazard assessment to determine the required PPE and safe work practices. | ☐ | ☐ | ☐ | ____________________ |
| Verify the secondary voltage of the transformer is within the specified range after installation. | ☐ | ☐ | ☐ | ____________________ |
| Ensure the neutral conductor is properly grounded at the transformer and at the service entrance. | ☐ | ☐ | ☐ | ____________________ |
| Verify correct phase rotation before energizing the transformer to prevent equipment damage. | ☐ | ☐ | ☐ | ____________________ |
| Balance the load across the phases to prevent overloading the transformer. | ☐ | ☐ | ☐ | ____________________ |

Documentation & Communication

| Item | Pass | Fail | N/A | Notes |
| --- | --- | --- | --- | --- |
| Conduct a thorough job briefing with all crew members before starting work. Discuss hazards, procedures, and emergency plans. | ☐ | ☐ | ☐ | ____________________ |
| Verify all required permits and approvals are obtained before commencing work. | ☐ | ☐ | ☐ | ____________________ |
| Record the transformer nameplate data (serial number, kVA rating, voltage) for future reference. | ☐ | ☐ | ☐ | ____________________ |
| Document the results of the pole inspection, including any defects found and corrective actions taken. | ☐ | ☐ | ☐ | ____________________ |
| Record the grounding resistance measurements for the bucket truck and transformer grounding systems. | ☐ | ☐ | ☐ | ____________________ |
| Maintain a record of all PCB-containing materials handled and disposed of, including quantities and disposal methods. | ☐ | ☐ | ☐ | ____________________ |
| Ensure all incidents and near misses are reported and investigated according to company policy. | ☐ | ☐ | ☐ | ____________________ |
| Maintain regular communication with dispatch to report progress and any changes in conditions. | ☐ | ☐ | ☐ | ____________________ |
| Notify affected customers of any planned outages or service interruptions. | ☐ | ☐ | ☐ | ____________________ |
| Conduct a post-installation inspection to verify all connections are secure and the transformer is operating properly. | ☐ | ☐ | ☐ | ____________________ |

Findings

| # | Item | Location | Severity | Action required |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |

Signature

Inspector signature: ______________________________    Name: ______________________________

Date: ______________________________